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	TECHNICAL REVIEW COMMITTEE MINUTES – SITE-2023-0013

	
		

	
	Application Type:
	Site Review

	
	Applicant(s):
	TF Moran

	
	Owner(s):
	256-264 Central Avenue, LLC

	
	Location:  
	256 & 264 Central Avenue (Tax Map 9, Lot 111 & 112)

	
	Date:
	November 30, 2023



INTENT: Proposal is to replace gravel parking with 10,595 square feet of paved parking related to their renovation of the buildings. This is Phase I of a two phase project.

UNITS PROPOSED:  n/a

AGENDA ITEM #: 2

ACREAGE:
Lot 111= 0.522± ac. / 22,747± sq. ft.
Lot 112= 0.167± ac. / 7,287± sq. ft.

ZONING DISTRICT:  CBD-G

EXISTING LAND USE:  Previously a Restaurant, Vacant building

PROPOSED LAND USE:  Commercial with Paved Parking; Phase I: Paved parking (Planned for future is Phase II: Renovation of the existing structures)

SURROUNDING LAND USE:  Commercial, Residential

ZBA ACTION: None

PERMITS REQUIRED:

WAIVERS REQUESTED: N/A

ATTENDANCE:
Members:
Donna Benton, Planning
Paul Crouser, Zoning
Marn Speidel, Police
Jim Maxfield, Fire/Inspection Services
Ken Mavrogeorge, Engineering
James Burdin, Business Development
Others:
Erin Bassegio, Planning
Derek Fisher, Owner
Chris Rice, TFMoran
Jason Cook, TFMoran




PLAN REVIEW: 
Planning:
· 71% lot coverage existing? 
· Revise plans: 
· Owner’s signatures on the final plans
· Add file number to plan set, SITE-2023-0013 to all sheets
· Professional stamps and signatures
· Add bench and waste bin (city standard)
· Discuss parking meter location with Parking Manager
· Add landscaping in lieu of street trees with waiver request
· Replace vinyl fence with stockade
· Confirm light fixtures meet downtown standard
· 
· Waiver request if applicable on final landscape design
· Letter to Serve (including EV readiness)
· Lot merger documentation to be submitted

Engineering: 
· Sheet C-02:
· Coordinate with IS on the location of the charger and whether it is ADA accessible. Suggest moving the ADA space to the northern space adjacent to the aisle. Grading to meet ADA slope requirements would likely be required.
· Recommend increasing the space behind the wheel stops to allow for accessible access to the charger. 
· Call out all curb radii (see connection to sidewalk).
· Please show location of proposed utility changes (water).
· Provide City standard water and drainage trench details or revise provided trench detail to show requirements for each type of service including bedding and backfill, cover, materials, etc.
· Sheet C-03:
· Test Pit and infiltration Test chart references stormtech chambers. Please revise.
· Add notes to call out the roof leaders, dimensions, and slopes.
· Sheet C-06:
· Recommend providing a minimum of 12-inch slab for dumpster pad. Please identify location of concrete pad detail.
· Sheet C-09:
· Check elevations on the outlet structure. The bottom of the pond does not appear correct.
· Drainage Analysis:
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· Recommend providing a flood elevation for the proposed structures in the calculations. 
· Applicant shall review the section 153-14 of the Dover Code and clarify how the design meets or exceeds the 
City’s requirements. More specifically applicant shall speak to how the proposed design meets the redevelopment criteria under 153-14(A)(3)(c), 153-14(A)(3(f).

Police:
· Dumpster truck movement plan looks tight
· Private property sign shown on plan-confirm location/intent

Fire/Inspection Services:
· Provide stamped set of plans
· Accessibility of EV charger-including minimum width access aisle, curb appears to be obstruction.
· Sheet C-02 Provide EV charger sign in sign legend. Also add sign detail to plan set
· Clarify the lot merger and sequence/phasing of project. 
· Sheet C-05 appears to have vegetation which may impede line of site, also appears to encroach on minimum distances from pad mount transformers

Business Development:
· Previous comments addressed. 

Planning Board: N/A

Next Steps: Review EV readiness with City staff and resubmit for Planning Board (January 23, 2024). 

Pause TRC at: 12:05 p.m.
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